## 100% BMCR (TD-BFP)
Turbine Driven Boiler Feed Water Pump |  |  | 100% BMCR 기준 (11/25 HBD.) | 2013.11.29
Basis / Input Parameters
Superheater outlet steam flow (BMCR) |  |  | kg/s | 875.141
Seconds per hour |  |  | s/h | 3600
BFP share ratio (2 x 60%) |  |  | - | 0.6
Miscellaneous (Attemp. spray) ratio |  |  | - | 0.025
Pump capacity margin (Surge5%+Wear6%) |  |  | - | 1.11
Specific gravity @ design temp |  |  | - | 0.87418
Design Flow
Item |  | unit | Source | Value
1) | Flow to boiler per BFP (2 x 60%) | kg/h | Superheater outlet 기준 (875.141*3600)*0.6
2) | Miscellaneous Flow | kg/h | Attemperator spray water (2.5% of 1)
3) | Total flow | kg/h | 1)+2)
4) | Pump capacity incl. margin | kg/h | 111% of 3)
5) | Design temp | 'C | BFP suction (HBD) | 191.7
6) | Specific gravity
7) | Pump Suction flow (Q1) | m3/h | 4) divide 6)
8) | Pump Discharge flow (Q2) | m3/h | 7)-9)
9) | Interstage Normal. flow | m3/h | 2) x 1.11(margin 11%) divide 6)
Discharge Head
Item |  |  | Source | Value
1) | Steam Turbine MSV inlet pressure | bar.a | HBD, BMCR 100% | 250
2) | P.D economizer inlet htr → Boiler SH outlet hdr | bar.a | Boiler data 참조 | 55.125
3) | P.D Boiler SH outlet hdr → ST MSV inlet | bar.a | Assume | 10.4738
4) | Superheater outlet Elevation | M | Boiler G.A 참조 | 81
5) | Pump Center Elevation | M | EBARA BFP 견적 참조 | 2.05
6) | Static head | bar.a | (4)-5))xs.g/10.2
7) | Pressure Drop flow nozzle | bar.a | KEPCO E&C Comment | 0.6
8) | Pressure Drop heater 6 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
9) | Pressure Drop heater 7 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
10) | Pressure Drop heater 8 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
11) | Pressure Drop Piping | bar.a | KEPCO E&C Comment | 10
12) | Calculated discharge P (PD) | bar.a | {1)+2)+3)+6)+7)+8)+9)+10)+11)}
Suction Head
Item |  |  | Source | Value
1) | Deaerator pressure (P1) | bar.a | HBD at BMCR | 13.03
2) | Deae. pres. fluct (PD1) | bar.a | P1 x 0.02
3) | Piping & valve PD incl. suction strainer (PD2) | bar.a | Assume | 0.5
4) | Deaerator EL (E1) | m | G.A | 23
5) | Pump center EL (E2) | m | EBARA BFP 견적 참조 | 2.05
6) | Static head (PH) | bar.a | (E1-E2)xS.G/10.2
7) | Suction Pressure (PS) | bar.a | P1-PD1-PD2+PH
| 포화증기압 (Sat. vapor pressure @191.7'C) | bar.a | Steam table | 13.0247
8) | NPSHa | bar.a | PS - 포화증기압
9) | NPSHa | m | bar.a to m
10) | selected NPSHa | m | round down
Pump Head and Power
Item |  |  | Source | Value
1) | Total development head | bar.a | PD-PS
2) | Total development head | m | (1)x10.2/S.G)*1.05 (Head margin 5%, MSF)

## 95% Load (Start-up)
Start-up Boiler Feed Water Pump Calculation |  |  | 95% Load, parallel operation | 2013.11.29
Basis / Input Parameters
Superheater outlet steam flow (BMCR) |  |  | kg/s | 875.141
Seconds per hour |  |  | s/h | 3600
Start-up load ratio (35% at BMCR) |  |  | - | 0.35
Pump capacity margin (Surge5%+Wear6%) |  |  | - | 1.11
Specific gravity @ design temp |  |  | - | 0.87418
Design Flow
Item |  | unit | Source | Value
1) | Flow to boiler from one (1x100%) Start-up BFP | kg/h | Superheater outlet 기준(35%) at BMCR (875.141*3600*0.35)
2) | Total flow | kg/h | 1)
3) | Pump capacity incl. margin (Surge5%+Wear6%) | kg/h | 111% of 2)
4) | Design temp | 'C | BFP suction (BMCR 100% 기준) | 191.7
5) | Specific gravity
6) | Pump Suction flow (Q1) | m3/h | 3) divide 5)
7) | Pump Discharge flow (Q2) | m3/h | 6)
Discharge Head
Item |  |  | Source | Value
1) | Steam Turbine MSV inlet pressure | bar.a | HBD | 250
2) | P.D economizer inlet htr → Boiler SH outlet hdr | bar.a | BMCR 100% P.D기준, 95%유량시 P.D | 45.125
3) | P.D Boiler SH outlet hdr → ST MSV inlet | bar.a | BMCR 100% P.D기준, 95%유량시 P.D | 8.5738
4) | Superheater outlet Elevation | M | Boiler G.A 참조 | 81
5) | Pump Center Elevation | M | EBARA BFP 견적 참조 | 2.05
6) | Static head | bar.a | (4)-5))xs.g/10.2
7) | Pressure Drop flow nozzle | bar.a | BMCR 100% P.D기준 | 0.6
8) | Pressure Drop heater 6 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
9) | Pressure Drop heater 7 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
10) | Pressure Drop heater 8 | bar.a | Heater 견적 참조 (less than 1.7) | 1.7
11) | Pressure Drop Piping | bar.a | BMCR 100% P.D기준, 95%유량시 P.D | 9.025
12) | Calculated discharge P (PD) | bar.a | {1)+2)+3)+6)+7)+8)+9)+10)+11)}
Suction Head
Item |  |  | Source | Value
1) | Deaerator pressure (P1) | bar.a | HBD | 13.03
2) | Deae. pres. fluct (PD1) | bar.a | P1 x 0.02
3) | Piping & valve PD incl. suction strainer (PD2) | bar.a | Assume | 0.5
4) | Deaerator EL (E1) | m | G.A | 23
5) | Pump center EL (E2) | m | EBARA BFP 견적 참조 | 2.05
6) | Static head (PH) | bar.a | (E1-E2)xS.G/10.2
7) | Suction Pressure (PS) | bar.a | P1-PD1-PD2+PH
| 포화증기압 (Sat. vapor pressure) | bar.a | Steam table | 13.0247
8) | NPSHa | bar.a | PS - 포화증기압
9) | NPSHa | m | bar.a to m
10) | selected NPSHa | m | round down
Pump Head and Power
Item |  |  | Source | Value
1) | Total development head | bar.a | PD-PS
2) | Total development head | m | (1)x10.2/S.G)x1.05 (Head margin 5%, MSF)

## 30% Load (Start-up)
Start-up Boiler Feed Water Pump Calculation |  |  | 30% Load, single operation | 2013.11.29
Basis / Input Parameters
TMCR 30% steam flow |  |  | kg/s | 240.163
Seconds per hour |  |  | s/h | 3600
Pump capacity margin (Surge5%+Wear6%) |  |  | - | 1.11
Specific gravity @ design temp |  |  | - | 0.91794
Design Flow
Item |  | unit | Source | Value
1) | Flow to boiler from one (1x100%) Start-up BFP | kg/h | HBD TMCR 30% load 기준 (240.163*3600)
2) | Total flow | kg/h | 1)
3) | Pump capacity incl. margin (Surge5%+Wear6%) | kg/h | 111% of 2)
4) | Design temp | 'C | BFP suction (HBD MCR 30%) | 149
5) | Specific gravity
6) | Pump Suction flow (Q1) | m3/h | 3) divide 5)
7) | Pump Discharge flow (Q2) | m3/h | 6)
Discharge Head
Item |  |  | Source | Value
1) | Steam Turbine MSV inlet pressure | bar.a | HBD 30% | 100
2) | P.D economizer inlet htr → Boiler SH outlet hdr | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 4.5
3) | P.D Boiler SH outlet hdr → ST MSV inlet | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 0.855
4) | Superheater outlet Elevation | M | Boiler G.A 참조 | 81
5) | Pump Center Elevation | M | EBARA BFP 견적 참조 | 2.05
6) | Static head | bar.a | (4)-5))xs.g/10.2
7) | Pressure Drop flow nozzle | bar.a | BMCR 100% P.D기준 | 0.6
8) | Pressure Drop heater 6 | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 0.153
9) | Pressure Drop heater 7 | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 0.153
10) | Pressure Drop heater 8 | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 0.153
11) | Pressure Drop Piping | bar.a | BMCR 100% P.D기준, 30%유량시 P.D | 0.9
12) | Calculated discharge P (PD) | bar.a | {1)+2)+3)+6)+7)+8)+9)+10)+11)}
Suction Head
Item |  |  | Source | Value
1) | Deaerator pressure (P1) | bar.a | 30% Load HBD | 4.64
2) | Deae. pres. fluct (PD1) | bar.a | P1 x 0.02
3) | Piping & valve PD incl. suction strainer (PD2) | bar.a | Assume | 0.5
4) | Deaerator EL (E1) | m | G.A | 23
5) | Pump center EL (E2) | m | EBARA BFP 견적 참조 | 2.05
6) | Static head (PH) | bar.a | (E1-E2)xS.G/10.2
7) | Suction Pressure (PS) | bar.a | P1-PD1-PD2+PH
| 포화증기압 (Sat. vapor pressure) | bar.a | Steam table | 4.6348
8) | NPSHa | bar.a | PS - 포화증기압
9) | NPSHa | m | bar.a to m
10) | selected NPSHa | m | round down
Pump Head and Power
Item |  |  | Source | Value
1) | Total development head | bar.a | PD-PS
2) | Total development head | m | (1)x10.2/S.G)x1.05 (Head margin 5%, MSF)