## Summary
Storage Tank Sizing Summary
No | Tank | Required Vw (m³) | Sel. D (m) | Sel. H (m) | H/D | Sel. Volume (m³) | Net Capacity (m³) | Result
1 | Condensate Storage Tank
2 | Service & Fire water Storage Tank
3 | Demi. water Storage Tank
4 | Fuel Oil Storage Tank
5 | Filtered Seawater Storage Tank

## Condensate
Calculation for Condensate Storage Tank
1. Design Condition
1) Tank type : Cone Roof
| 3) Tank ID |  |  | 11.6 | m
2. Calculation
| ∴ Working Capacity (Vw) = |  |  | 568 | m³ | 대당 =
HH = Top level - High level
Hw = High level - Low level (Working Volume)
HL = Low level - Bottom level
2) Normal Capacity (Vn)
→ Working capacity + Dead capacity
Dead capacity (V0) = (HL + HH) x D²/4
- HW
| → Seismic Zone |  |  | HW | = | 0.46 | x D
|  |  |  | D | = |  | m
|  |  |  | HW | = |  | m
|  |  |  | Q | = |  | m³
- HL
| 1) Tank Bottom to Outlet Nozzle Center Line dim. (Regular Type) |  |  | 12 | " | = |  | mm
| 2) Top outlet nozzle over |  |  |  |  | = | 150 | mm
| 3) Outlet nozzle radius |  |  |  |  | = | 1000 | mm
|  | HL | = |  | mm | Application = |  | m
- HH
| Cone roof case tank top to extinguishing agent discharge outlet | [5 empty] | 300 | mm
| HH level to extinguishing agent discharge | [5 empty] | 600 | mm
|  | HH | = |  | m
|  | Dead Capacity = |  |  | m³
|  | So, Nominal capacity = |  |  | m³
|  | HT = |  |  | m
| H = selected (attach#1) |  |  |  | H/D :
|  | H | = | 7.75 | m
|  | D | = | 11.63 | m
|  | Volume | = | 822.82 | m³
|  |  | HH |  | HL
|  |  |  | m |  | m
| Dead Capacity : |  |  | m³ |  | m³
| Design Capacity (Net Capacity) : |  |  |  |  | m³
Check (Net ≥ Required Vw) :

## Service&Fire
Calculation for Service & Fire water Storage Tank
1. Design Condition
1) Tank type : Cone Roof
| 3) Tank ID |  |  | 24.3 | m
2. Calculation
| ∴ Working Capacity (Vw) = |  |  | 6400 | m³ | 대당 =
HH = Top level - High level
Hw = High level - Low level (Working Volume)
HL = Low level - Bottom level
2) Normal Capacity (Vn)
→ Working capacity + Dead capacity
Dead capacity (V0) = (HL + HH) x D²/4
- HW
| → Seismic Zone |  |  | HW | = | 0.57 | x D
|  |  |  | D | = |  | m
|  |  |  | HW | = |  | m
|  |  |  | Q | = |  | m³
- HL
| 1) Tank Bottom to Outlet Nozzle Center Line dim. (Regular Type) |  |  | 15 | " | = |  | mm
| 2) Top outlet nozzle over |  |  |  |  | = | 150 | mm
| 3) Outlet nozzle radius |  |  |  |  | = | 1000 | mm
|  | HL | = |  | mm | Application = |  | m
- HH
| Cone roof case tank top to extinguishing agent discharge outlet | [5 empty] | 300 | mm
| HH level to extinguishing agent discharge | [5 empty] | 600 | mm
|  | HH | = |  | m
|  | Dead Capacity = |  |  | m³
|  | So, Nominal capacity = |  |  | m³
|  | HT = |  |  | m
| H = selected (attach#1) |  |  |  | H/D :
|  | H | = | 16.34 | m
|  | D | = | 24.27 | m
|  | Volume | = | 7556.38 | m³
|  |  | HH |  | HL
|  |  |  | m |  | m
| Dead Capacity : |  |  | m³ |  | m³
| Design Capacity (Net Capacity) : |  |  |  |  | m³
Check (Net ≥ Required Vw) :

## Demi
Calculation for Demi. water Storage Tank
1. Design Condition
1) Tank type : Cone Roof
| 3) Tank ID |  |  | 17.7 | m
2. Calculation
| ∴ Working Capacity (Vw) = |  |  | 2300 | m³ | 대당 =
HH = Top level - High level
Hw = High level - Low level (Working Volume)
HL = Low level - Bottom level
2) Normal Capacity (Vn)
→ Working capacity + Dead capacity
Dead capacity (V0) = (HL + HH) x D²/4
- HW
| → Seismic Zone |  |  | HW | = | 0.53 | x D
|  |  |  | D | = |  | m
|  |  |  | HW | = |  | m
|  |  |  | Q | = |  | m³
- HL
| 1) Tank Bottom to Outlet Nozzle Center Line dim. (Regular Type) |  |  | 17 | " | = |  | mm
| 2) Top outlet nozzle over |  |  |  |  | = | 150 | mm
| 3) Outlet nozzle radius |  |  |  |  | = | 1000 | mm
|  | HL | = |  | mm | Application = |  | m
- HH
| Cone roof case tank top to extinguishing agent discharge outlet | [5 empty] | 300 | mm
| HH level to extinguishing agent discharge | [5 empty] | 600 | mm
|  | HH | = |  | m
|  | Dead Capacity = |  |  | m³
|  | So, Nominal capacity = |  |  | m³
|  | HT = |  |  | m
| H = selected (attach#1) |  |  |  | H/D :
|  | H | = | 11.87 | m
|  | D | = | 17.68 | m
|  | Volume | = | 2913.57 | m³
|  |  | HH |  | HL
|  |  |  | m |  | m
| Dead Capacity : |  |  | m³ |  | m³
| Design Capacity (Net Capacity) : |  |  |  |  | m³
Check (Net ≥ Required Vw) :

## FuelOil
Calculation for Fuel Oil Storage Tank
1. Design Condition
1) Tank type : Cone Roof
| 3) Tank ID |  |  | 19.3 | m
2. Calculation
| ∴ Working Capacity (Vw) = |  |  | 3000 | m³ | 대당 =
HH = Top level - High level
Hw = High level - Low level (Working Volume)
HL = Low level - Bottom level
2) Normal Capacity (Vn)
→ Working capacity + Dead capacity
Dead capacity (V0) = (HL + HH) x D²/4
- HW
| → Seismic Zone |  |  | HW | = | 0.53 | x D
|  |  |  | D | = |  | m
|  |  |  | HW | = |  | m
|  |  |  | Q | = |  | m³
- HL
| 1) Tank Bottom to Outlet Nozzle Center Line dim. (Regular Type) |  |  | 20 | " | = |  | mm
| 2) Top outlet nozzle over |  |  |  |  | = | 150 | mm
| 3) Outlet nozzle radius |  |  |  |  | = | 1000 | mm
|  | HL | = |  | mm | Application = |  | m
- HH
| Cone roof case tank top to extinguishing agent discharge outlet | [5 empty] | 300 | mm
| HH level to extinguishing agent discharge | [5 empty] | 600 | mm
|  | HH | = |  | m
|  | Dead Capacity = |  |  | m³
|  | So, Nominal capacity = |  |  | m³
|  | HT = |  |  | m
| H = selected (attach#1) |  |  |  | H/D :
|  | H | = | 12.84 | m
|  | D | = | 19.32 | m
|  | Volume | = | 3761.78 | m³
|  |  | HH |  | HL
|  |  |  | m |  | m
| Dead Capacity : |  |  | m³ |  | m³
| Design Capacity (Net Capacity) : |  |  |  |  | m³
Check (Net ≥ Required Vw) :

## Seawater
Calculation for Filtered Seawater Storage Tank
1. Design Condition
1) Tank type : Cone Roof
| 3) Tank ID |  |  | 11.2 | m
2. Calculation
| ∴ Working Capacity (Vw) = |  |  | 500 | m³ | 대당 =
HH = Top level - High level
Hw = High level - Low level (Working Volume)
HL = Low level - Bottom level
2) Normal Capacity (Vn)
→ Working capacity + Dead capacity
Dead capacity (V0) = (HL + HH) x D²/4
- HW
| → Seismic Zone |  |  | HW | = | 0.45 | x D
|  |  |  | D | = |  | m
|  |  |  | HW | = |  | m
|  |  |  | Q | = |  | m³
- HL
| 1) Tank Bottom to Outlet Nozzle Center Line dim. (Regular Type) |  |  | 10 | " | = |  | mm
| 2) Top outlet nozzle over |  |  |  |  | = | 150 | mm
| 3) Outlet nozzle radius |  |  |  |  | = | 1000 | mm
|  | HL | = |  | mm | Application = |  | m
- HH
| Cone roof case tank top to extinguishing agent discharge outlet | [5 empty] | 300 | mm
| HH level to extinguishing agent discharge | [5 empty] | 600 | mm
|  | HH | = |  | m
|  | Dead Capacity = |  |  | m³
|  | So, Nominal capacity = |  |  | m³
|  | HT = |  |  | m
| H = selected (attach#1) |  |  |  | H/D :
|  | H | = | 7.45 | m
|  | D | = | 11.23 | m
|  | Volume | = | 737.51 | m³
|  |  | HH |  | HL
|  |  |  | m |  | m
| Dead Capacity : |  |  | m³ |  | m³
| Design Capacity (Net Capacity) : |  |  |  |  | m³
Check (Net ≥ Required Vw) :